## SCOPE OF WORK

Project Title:
DX to CHW Conversion – Student Center Library Building

Project Overview:
This project intends to convert the existing Direct Expansion (DX) cooling system serving three (3) multi-zone Air Handling Units (AHUs) at the Student Center Library Building to a Chilled Water (CHW) cooling system. The work includes design, fabrication, testing, delivery, installation, and commissioning of new CHW coils and associated components in accordance with the technical specifications provided in Attachment A – Section 23 73 24 Custom Air Handling Unit Specifications.

The selected Contractor shall furnish all labor, materials, equipment, and supervision necessary to complete the work described herein.

### 1. GENERAL REQUIREMENTS

1.1. Contractor shall be responsible for the design, fabrication, testing, cleaning, packaging, shipment, final assembly, and installation of all mechanical components and systems required to complete the DX-to-CHW conversion.
1.2. All work shall be performed in compliance with applicable local, state, and federal codes and regulations, as well as the College’s technical specifications and safety policies.
1.3. Any omissions or discrepancies in the contract documents shall be clarified in writing with the College before proceeding with the work, per Section 2 of the RFP.
1.4. The project shall include full integration of all three AHUs and associated heating systems into the building’s existing Building Automation System (BAS) for monitoring, control, and energy optimization.

### 2. DEMOLITION AND REMOVAL

2.1. Contractor shall remove and properly dispose of all components associated with the existing DX refrigerant systems serving the multi-zone AHUs, including but not limited to coils, compressors, condensers, and refrigerant piping.
2.2. Disposal shall comply with all applicable EPA, state, and local environmental guidelines.
2.3. Reference Attachment B – Existing Equipment Photos and Data Plates for identification of existing systems.

### 3. CHILLED WATER COIL INSTALLATION

3.1. Contractor shall design, fabricate, and install new chilled-water coils within the existing built-up AHU housings.
3.2. The new coil assemblies shall:

- Meet or exceed the requirements outlined in Attachment A – Section 23 73 24 Custom AHU Specifications.

- Match existing airflow and capacity to maintain design conditions for all zones served.
3.3. All below-roof air distribution systems are excluded from this scope except where necessary to connect new units to existing ductwork.
3.4. Contractor shall perform the following related tasks:

- Clean all associated ductwork prior to reassembly.

- Perform airflow testing and balancing (TAB) after installation.

- Reconnect and test all existing fire damper controls to ensure proper operation with the AHU controller.

### 4. BUILDING AUTOMATION AND CONTROLS

4.1. Existing building controls are Distech brand.
4.2. Contractor shall furnish and install new Distech unit controllers for each AHU and perform full BAS integration, including:

- Programming, graphics, and sequence of operations for all new components.

- Incorporation of CO₂-based demand-control ventilation for classrooms and laboratory zones.

- Full point-to-point verification and control calibration.

### 5. CHILLED WATER AND HEATING CONNECTIONS

5.1. Contractor shall extend CHW supply and return piping to the roof to serve each AHU.
5.2. Contractor is responsible for:

- All piping, valves, fittings, insulation, and controls.

- Structurally approved pipe supports and rooftop penetrations.
5.3. Heating System:

- Existing heating is provided by natural-gas furnace sections within each AHU.

- These sections shall be retained and reused in their current configuration.

### 6. ANCILLARY SYSTEMS

6.1. Any existing air ionization or air-cleaning systems shall be safely removed prior to coil replacement and reinstalled after work completion.
6.2. Contractor shall verify all systems are restored to full functionality prior to turnover.

### 7. START-UP, TESTING, AND COMMISSIONING

7.1. Contractor shall provide complete start-up, testing, and documentation for all new systems and components.
7.2. Documentation shall include:

- Factory test results

- Installation checklists

- As-built drawings

- Sequence of operations and control logic

- Equipment submittals and O&M manuals
7.3. Following start-up, the College will engage a third-party commissioning agent to perform independent functional testing and point-to-point verification prior to project closeout. Contractor shall provide full cooperation and access to the commissioning team.

### 8. CLEANUP AND CLOSEOUT

8.1. Contractor shall maintain a clean worksite throughout the project and remove all debris upon completion.
8.2. Submit all required closeout documents, including warranty certificates, test reports, and final as-builts, before final acceptance.

### 9. EXCLUSIONS

- Any modifications to zone-level ductwork beyond necessary connections.

- Replacement of gas furnace sections.

- Electrical infrastructure upgrades beyond local connections to new equipment unless specified.

- Structural upgrades not directly related to coil or piping supports.

Patrick Shahnazarian

Facilities Department

1500 N Verdugo Rd Glendale California 91208

818 240 1000 - 6610