# SECTION 23 73 24 – AIR HANDLING UNITS – DX-TO-CHW CONVERSION (RETROFIT)

## PART 1 – GENERAL

### 1.01 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General Conditions and Division 01, apply to this Section.
B. Specifications throughout all Divisions are directly applicable to this Section, and this Section is directly applicable to them.
C. Coordinate with Division 23 (Mechanical), Division 26 (Electrical), Division 25 (Integrated Automation/BAS), and Division 01 commissioning requirements.

### 1.02 SUMMARY

A. Work includes all labor, materials, equipment, services, and incidentals to convert existing DX cooling within three (3) multi-zone AHUs to chilled-water (CHW) cooling, including:

- Safe recovery and disposal of refrigerant; demolition/removal of existing DX coils, compressors, condensers, and associated refrigerant piping.

- Design, fabrication, delivery, and installation of new CHW cooling coils and accessories to fit the existing built-up AHU casings.

- Extension/connection of CHW supply/return to rooftop AHUs, including valves, strainers, balancing valves, control valves/actuators, insulation, and structurally approved pipe supports.

- Controls upgrades to integrate all three AHUs (cooling and existing heating sections) to the existing Distech BAS, including sequences, graphics, point mapping, trending, and demand-control ventilation (DCV) for classroom/lab zones (CO₂).

- Cleaning of associated duct sections impacted by the retrofit; post-installation TAB of air and water.

- Start-up, functional testing support, O&M documentation, and closeout. Third-party commissioning is by Owner.

B. This Section applies to retrofit work within existing AHUs. Where the Drawings schedule a fan array section or other specialty sections, the related paragraphs herein apply; otherwise, retain existing fans unless specifically indicated.

### 1.03 REFERENCE STANDARDS

A. Latest published editions at time of bid, unless a specific edition/date is listed on the Drawings.
B. Where conflicts occur, the more stringent requirement governs.
C. Applicable standards include, but are not limited to:

- AMCA 99, 210, 300, 301, 500.

- AHRI 260 (Sound), AHRI 410 (Coils), AHRI 430 (Central Station AHUs), AHRI 611 (Humidifiers) or as scheduled.

- ASHRAE 52.2 (Filters), ASHRAE 62.1 (Ventilation/IAQ), ASHRAE 90.1 (Energy).

- NFPA 70 (NEC); NFPA 90A.

- NFPA 262 (CMP/Plenum Cable).

- SMACNA HVAC Duct Construction Standards.

- UL 900 (Air Filter Units).

- EPA 40 CFR Part 82 / Section 608 (Refrigerant Recovery/Handling).

- IBC/IMC/IFC as adopted by Authority Having Jurisdiction (AHJ).

### 1.04 QUALITY ASSURANCE

A. Manufacturer(s): Minimum 5 years’ experience producing the specified coils and AHU components; publish complete product data.
B. Performance Ratings: Conform to AHRI 430/410 as applicable; units/coil selections to be certified or factory-tested to the referenced standards.
C. Sound Ratings: Test per AMCA 300 and AHRI 260.
D. Coils: Certify capacities, pressure drops, and selections per AHRI 410.
E. Environmental Conditions: Components suitable for 35–135°F ambient; 20–70% RH (conditioned spaces), up to 100% RH (unconditioned mechanical rooms).
F. Fit/Access: New components shall fit existing AHU housings with required service clearances. Submittals that do not fit the allocated space shall be rejected.
G. Refrigerant Handling: Perform recovery, cylinder handling, transport, and disposal by EPA Section 608-certified personnel; provide chain-of-custody/disposal documentation.

### 1.05 SUBMITTALS

A. Product Data and Shop Drawings:

- Dimensions, weights, coil face areas/rows/fins-per-inch (FPI), connection sizes/locations, materials/finishes, design/operating pressures and temperatures.

- Coil selections with entering/leaving air and water conditions, GPM, PD (water and air), and safety factors; certify per AHRI 410.

- Fan data (if fans are replaced or a fan array is scheduled): fan curves at the design operating point including system effects; sound power levels (inlet/outlet/casing) per AMCA/AHRI.

- Sound data for the assembled AHU retrofit not to exceed scheduled limits.

- Controls/BAS: control diagrams, points list, sequences of operation (cooling/heating, economizer if applicable, DCV/CO₂ logic, alarms), graphics examples, network topology, and I/O schedules.

- Electrical power requirements and wiring diagrams clearly differentiating factory vs. field wiring; identify all penetrations/taps and TAB ports on drawings.

- Note each deviation from Contract Documents and state reason.
B. O&M Manuals: installation instructions, start-up procedures, maintenance, parts lists, coil cleaning procedures, recommended spares, and as-built control sequences/graphics screens.
C. Closeout: factory test records, start-up forms, TAB reports (air and water), warranty certificates, and BAS point-to-point checkout forms.

### 1.06 EXTRA MATERIALS

A. Per Section 01 78 46 — provide recommended spare filters (one full change per AHU), one set of BAS sensors (CO₂ and temperature) per AHU, and (if arrays are provided) one spare fan motor per nominal HP used in the array.

### 1.07 DELIVERY, STORAGE, AND HANDLING

A. Deliver in factory packaging with listed lifting points/lugs; inspect upon receipt.
B. Store clean/dry; protect from weather and construction dust. Seal all casing openings; cap/plug coil connections.
C. Prevent damage to coatings, insulation, and fins. Replace damaged components at no cost to Owner.

### 1.08 SCHEDULES ON DRAWINGS

A. Capacities, flows, pressures, sound limits, and electrical data are scheduled on the Drawings; these are minimum performance requirements. Deviations require written approval by Owner and Engineer.
B. Where multiple like items occur (coils, filters, valves), use single manufacturer where practicable.
C. Follow manufacturer’s installation instructions where not otherwise detailed.
D. Motor and wheel diameters shown are maximums unless otherwise noted.

## PART 2 – PRODUCTS

### 2.01 GENERAL

A. Materials shall meet or exceed referenced standards and local/state/federal requirements.
B. Provide permanent labels/tags for service and safety identification.
C. Provide complete retrofit assemblies and accessories required to achieve scheduled performance within existing AHU casings.
D. Configuration: Coil sections, access plenums, filters (pre/final as scheduled), drain pans, doors, dampers, sensors, valves/actuators, and (where scheduled) fan array sections and VFDs.
E. Fabrication: Conform to AMCA 99 where not otherwise specified.
F. Performance parameters: As scheduled on Drawings.
G. Footprint/Access: Retrofit assemblies shall not increase unit footprint beyond available space or obstruct service clearances.

### 2.02 MANUFACTURERS

A. Coils: Coilmaster; Super Radiator Coils; Modine; Temtrol/Daikin; or equal meeting this Section.
B. Fan Arrays (if scheduled): ClimateCraft; Energy Labs; Haakon; Huntair/Temtrol; Trane; York (JCI).
C. BAS Controllers: Distech (to match existing); sensors/actuators compatible with existing BAS platform.

### 2.03 AHU CASING/FRAME (EXISTING) AND RETROFIT ASSEMBLIES

A. Existing AHU casings will be reused. New coil racks, intermediate drain pans, access sections, and penetrations shall maintain or improve existing casing leakage class (≤ 0.5 cfm/ft² at scheduled static).
B. All new penetrations shall be factory- or shop-prepared and fully gasketed/sealed (no unsealed field penetrations).
C. Provide new IAQ drain pans (Type 304 stainless) under cooling coils, meeting ASHRAE 62.1: triple-slope to drains, extended downstream as required to capture carryover; insulate undersides with closed-cell foam (minimum R-14).
D. Floors/bases within retrofit sections shall be non-through-metal (thermal break) and insulated to avoid condensation.
E. Access doors: double-wall insulated, thermal-break frames, full swing, latch/hinge count per door size, with gasketed viewports; locate to provide coil, filter, and drain pan service.

### 2.04 FANS AND DRIVES (ONLY WHERE SHOWN ON DRAWINGS)

A. Where scheduled to replace or supplement existing fans, provide direct-drive plenum fan arrays (arrangement 4) sized so design operation does not exceed 90% of fan peak static capability at design speed.
B. Provide backdraft isolation per fan cube, airflow measurement for at least one cube per array (4–20 mA or 0–10 V output to BAS), dynamic/static balancing per AMCA 204-96 Grade 2.5, and VFD control for A/B groupings if specified.
C. Motors: premium efficiency, inverter duty with shaft grounding/isolated bearings; sealed bearings, continuous operation 0–120 Hz (when required); nameplate voltage/HP as scheduled.

### 2.05 COIL SECTION (CHILLED WATER AND HOT WATER WHERE APPLICABLE)

A. Coil Casing/Racks:

- Retrofit coil racks to allow individual coil removal; CHW coil racks Type 304 stainless; HW racks hot-dip galvanized carbon steel minimum.

- Factory pre-piped within coil section to the extent feasible; neatly seal all penetrations.
B. Chilled-Water Coils:

- AHRI 410 certified selections at scheduled conditions; provide submittal printouts with entering/leaving air/water, GPM, air and water PD.

- Tubes: 5/8-inch OD copper, minimum 0.035-inch wall; fins copper or aluminum as scheduled; mechanically expanded bond.

- Rows/FPI as scheduled; if additional capacity is required, provide two coil banks in series with an access section between; pipe counter-flow to airstream.

- Headers: brass or seamless copper with recessed/formed penetrations; supply/return with flanged or grooved ends as coordinated.

- Ratings/Tests: 300 psig working pressure; hydrostatic/air-under-water test to 325 psig minimum. Stainless steel coil nameplate with manufacturer, model, media, test pressure, and max operating limits.
C. Hot-Water Coils (if scheduled): copper tubes 5/8-inch OD (0.025-inch min wall; 0.035-inch if preheat/freezestat duty), aluminum fins; same-end connections unless noted.
D. Steam Coils: Not in base scope; provide only if scheduled on the Drawings.
E. Freezestat: Provide low-limit freezestat across CHW coil face; coordinate auto-reset/manual-reset as specified in controls.

### 2.06 FILTER SECTION

A. Filters per Section 23 40 00; MERV ratings per Drawings (ASHRAE 52.2).
B. Provide frames and gasketing to prevent bypass; max filter width 24 inches.
C. Provide one (1) boxed set of pre- and final filters per AHU for Owner (ship inside unit); Contractor to install new filters prior to start-up and a final clean set at Substantial Completion.
D. Provide differential pressure taps/ports and BAS points for filter loading.

### 2.07 VALVES, SPECIALTIES, AND ACCESSORIES (ADDED FOR RETROFIT)

A. CHW: combination balance/isolation valves, circuit setters, pressure/temperature ports, Y-strainers with blow-down, control valves with electronic actuators compatible with Distech BAS.
B. Condensate: traps sized for unit negative pressure, priming means, and ¼ in/ft slope to designated drain.
C. Insulation: piping/valves/strainers per Division 23 insulation section; vapor-tight jackets in plenums.
D. Pipe Supports: roof-approved supports with structural review where required by AHJ.

### 2.08 CONTROLS/BAS INTEGRATION

A. Distech controllers to match existing BAS; provide new unit controllers, I/O modules, sensors (space CO₂ and temperature as required), actuators, and network integration.
B. Sequences (minimum): CHW valve control to discharge-air or zone reset; heating section enable/disable and discharge reset; supply fan VFD control (if provided); DCV using CO₂ for classroom/lab zones; filter/coil frost alarms; unit safeties (freezestat, smoke detector interlocks per NFPA 90A).
C. Provide full graphics, trends, alarms, schedules, and hard-wired interlocks where specified (gateways/interfaces only when approved).
D. Provide points list and point-to-point checkout forms for commissioning.

## PART 3 – EXECUTION

### 3.01 EXAMINATION

A. Verify existing AHU conditions, clearances, coil pull paths, access, and structural supports prior to fabrication. Field-measure and coordinate all coil connection locations.

### 3.02 DEMOLITION

A. Recover refrigerant and provide disposal manifest per EPA 608. Remove DX coils, compressors, condensers, and refrigerant piping slated for demolition; cap abandoned services as required. Protect existing AHU sections to remain.

### 3.03 INSTALLATION

A. Install coils, racks, drain pans, valves, and specialties plumb and true; maintain service clearances.
B. Provide sealed/gasketed penetrations; maintain casing leakage class.
C. Pipe CHW supply/return to units with isolation, strainers, balance valves, and control valves; label per Division 23/26.
D. Reinstall any existing air ionization systems after coil work and verify operation.

### 3.04 CLEANING, TAB, AND START-UP

A. Clean coil fins and adjacent duct sections impacted by work prior to TAB.
B. Hydronic TAB: set design GPM and document PD; Air TAB: set design CFM and verify zone deliveries.
C. Start-up: complete manufacturer checklists; verify drain pan slope/traps; verify freezestat and safeties; document trend logs.

### 3.05 CONTROLS/BAS

A. Implement approved sequences; integrate points; furnish graphics; verify alarms/trends; perform point-to-point testing with Owner’s representative.

### 3.06 COMMISSIONING

A. Support Owner’s third-party commissioning (functional testing, issue resolution). Provide access, trending, and corrective actions. Commissioning by Owner occurs after Contractor start-up and submittal of documentation.

### 3.07 CLOSEOUT

A. Submit as-builts (mechanical, controls), O&M manuals, start-up/TAB reports, warranties, and EPA 608 refrigerant documentation. Provide training for Owner staff (minimum 4 hours per AHU group).

### 3.08 WARRANTY

A. Minimum 1-year labor/materials; coils 2-years against leaks/manufacturing defects; controls 2-years; motors/VFDs per manufacturer, not less than 18 months from start-up.

### Exclusions (clarification)

- Zone-level duct modifications beyond fit-up.

- Replacement of gas furnace sections unless noted.

- Electrical feeder upgrades beyond local connections.

- Structural upgrades not directly required for pipe supports or unit service.

Patrick Shahnazarian

Facilities Department

1500 N Verdugo Rd Glendale California 91208

818 240 1000 - 6610